## Summary
Rough power consumption list
SUMMARY OF LOAD CALCULATION
S NO. | DESCRIPMON | CONN. LOAD {kW} | DEMAND FACTOR | MAX. DEMAND {kW} | REMARKS
1 | HVAC | 505.71 | 0.65 | 328.7115
2 | PLUMBING | 42.4 | 0.5 | 21.2
3 | WATER BODY-1,2,3,4,5,6 & Pool | 184 | 0.5 | 92
4 | GROUND & FIRST FLOOR POWER & LIGHT | 41.6 | 0.6 | 24.96
5 | KITCHEN | 70.7 | 0.4 | 28.28
6 | LIFT | 8 | 0.6 | 4.8
7 | TERRACE FLOOR POWER & LIGHT | 3 | 0.5 | 1.5
8 | LANDSCAPE LIGHT | 15.0575 | 0.6 | 9.0345
9 | LANDSCAPE POWER | 71.56 | 0.6 | 42.936
10 | INTERNAL LIGHT LOAD | 18.3453 | 0.6 | 11.0072
11 | AUDIO SYSTEM | 90.9 | 0.5 | 45.45
12 | AUTOMATION SOCKET | 6.78 | 0.6 | 4.068
| TOTAL LOAD KW | 1058.0528 |  | 613.9472
| DEMAND LOAD | 613.9472 |  |  | 500kVA, 11/0.433 KV, OIL- COOLED TRANSFORMER WITH OLTC
| LOAD FACTOR | 0.65
| MAX DEMAND LOAD (kW) | 399.0657
| POWER FACTOR: | 0.9
| TOTAL LOAD DEMAND IN kVA | 443.4063
| WITH 5% SAFETY MARGIN | 22.1703
| TOTAL FINAL DEMAND LOAD IN kVA | 465.5766
| REQUIRED TRANSFORMER IN kVA | 500 |  |  |  | OLTC
DG SET SELECTION
| Maximum Demand Load (kW) | 613.9472
| Load factor | 0.65
| Maximum Demand Load (kW) | 399.0657
| DG Power Factor | 0.8
| Total Maximum Demand (kVA) | 498.8321
| REQUIRED DG 1 & 2:- 250 kVA ( 2 SETS ) | 200 |  |  | EQUALLY LOADED | 250kVA 2 NOS
| SERVO |  |  | WE ARE PROPSING TRX-WITH OLTC. PLEASE CONFIRM IF SERVO STILL REQUIRED.
| Maximum Demand Load (kVA) | 465.5766
| SERVO STABILIZER REQUIRED IN kVA | 500 |  | TECHNICALLY SERVO NOT REQUIRED
HT CONNECTION REQUIRED
| TOTAL LOAD DEMAND IN kVA | 443.4063
| PF | 0.9
| HT CONNECTION REQUIRED FROM ELECTRICITY COMPANY | 399.0657 |  |  | 11 kV HT BULK METERING
1 | 30X30 KVA 2NO. UPS REQUIRED FOR AUTOMATION LIGHTING & AUDIO VIDEO | 60 |  |  | AS PER DISSCUSED WITH ALDRIZ & GOLDY JI
| CAPACITOR BANK | 175 kVAR |  |  | POWER 0.85 > 0.98

## HVAC
Rough power consumption list | ELECTRICAL DATA SHEET
| Area | TYPE OF EQUIPMENT | CFM | TR | Input KW | Unit |  | Total | ELECTRICAL DATA
[5 empty] | Per Unit | Qty. | Phase | Input KW | MCB (Amp) | ELCB (Amp) (300mA,4-Pole) | STARTAR | Cable Size
CKT - 1
GROUND FLOOR
1 | MASTER TOI BATH+DRESS+WIW -1 | ROOF TOP UNIT | 2116 | 5.69 | 1.5 | 1 | Three Phase | 1.49 |  |  | SUTABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
2 | MASTER BEDROOM 2 & LOUNGE | ROOF TOP UNIT | 2298 | 6.23 | 2.2 | 1 | Three Phase | 2.24 |  |  | SUTABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| MASTER TOI BATH+DRESS+WIW -2 | ROOF TOP UNIT | 1874 | 4.93 | 1.5 | 1 | Three Phase | 1.49 |  |  | SUTABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| MASTER BEDROOM 1 & LOUNGE | ROOF TOP UNIT | 2116 | 5.69 | 1.5 | 1 | Three Phase | 1.49 |  |  | SUTABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 36 HP VRV OUTDOOR | TOP DISCHARGE |  | 18 HP | 15.5 | 1 | Three Phase | 15.5 |  | 40X1 |  | 4C X ( 10 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
|  |  |  | 18 HP | 15.5 | 1 | Three Phase | 15.5 |  | 40X1 |  | 4C X ( 10 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| IDU / ODU K.W ( CKT -1) | [6 empty] | 37.71
CKT - 2
4 | GURUJI ROOM & STORE -2 | ROOF TOP UNIT | 1767 | 4.61 | 1.5 | 1 | Three Phase | 1.5 |  |  | SUTABLE FOR -1.49 KW MOTOR | 4C X ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
5 | GURUJI TOI BATH+DRESSING | ROOF TOP UNIT | 1002 | 2.52 | 0.8 | 1 | Three Phase | 0.8 |  |  | SUTABLE FOR -.75 KW MOTOR | 4C X ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
4 | GUEST BEDROOM 1+STORE | ROOF TOP UNIT | 1695 | 4.4 | 1.5 | 1 | Three Phase | 1.5 |  |  | SUTABLE FOR -1.49 KW MOTOR | 4C X ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
5 | GUEST TOI BATH + DRESS -1 | ROOF TOP UNIT | 1332 | 3.4 | 1.1 | 1 | Three Phase | 1.1 |  |  | SUTABLE FOR -1.12 KW MOTOR | 4C X ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
5 | BAR AREA LOBBY+POWDER TOI | ROOF TOP UNIT | 3754 | 10.49 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUTABLE FOR -1.24 KW MOTOR | 4C X ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 44 HP VRV OUTDOOR | TOP DISCHARGE |  | 22 HP | 15.5 | 2 | Three Phase | 31 |  | 63X2 |  | 4CX ( 16 Sqmm Cu).x 2 No with Neutral +Earth.- 2 No
| IDU / ODU K.W ( CKT -2) | [6 empty] | 38.1
CKT - 3
6 | DOUBLE HEIGHT ENTERNCE | ROOF TOP UNIT | 2261 | 6.12 | 1.5 | 1 | Three Phase | 1.5 |  |  | SUTABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
7 | PUJA AREA UNIT-1 | ROOF TOP UNIT | 2417 | 6.54 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUTABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
6 | PUJA AREA UHIT-2 | ROOF TOP UNIT | 2417 | 6.54 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUTABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
7 | PASSAGE+DOUBLE HEIGHT -4 | ROOF TOP UNIT | 5886 | 16.55 | 3.7 | 1 | Three Phase | 3.7 |  |  | SUTABLE FOR -3.73 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 56 HP VRV OUTDOOR | TOP DISCHARGE |  | 20 HP | 17.9 | 2 | Three Phase | 35.8 |  | 63X2 |  | 4CX ( 16 Sqmm Cu).x 2 No with Neutral +Earth.- 2 No
|  | TOP DISCHARGE |  | 14 HP | 10.6 | 1 | Three Phase | 10.6 |  | 32X1 |  | 4CX ( 16 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| IDU / ODU K.W ( CKT -3) | [6 empty] | 56
CKT - 4
8 | PLAY / STUDY AREA | ROOF TOP UNIT | 2316 | 6.28 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUTABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
9 | DINING AREA & LOBBY,POWDER | ROOF TOP UNIT | 2536 | 6.89 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUTABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
10 | FAMILY LOUNGE | ROOF TOP UNIT | 3232 | 8.99 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUTABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| FORMAL LIVING ROOM | ROOF TOP UNIT | 3119 | 8.65 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 46 HP VRV OUTDOOR | TOP DISCHARGE |  | 20 HP | 17.9 | 1 | Three Phase | 17.9 |  | 63X1 |  | 4C X ( 16 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
|  |  |  | 26 HP | 19.9 | 1 | Three Phase | 19.9 |  | 63X1 |  | 4C X ( 16 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| IDU / ODU K.W ( CKT -4) | [6 empty] | 46.6
CKT - 5
11 | PASSAGE+DOUBLE HEIGHT -1 | ROOF TOP UNIT | 5886 | 16.55 | 3.7 | 1 | Three Phase | 3.7 |  |  | SUITABLE FOR -3.73 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
12 | PASSAGE+DOUBLE HEIGHT -2 | ROOF TOP UNIT | 5886 | 16.55 | 3.7 | 1 | Three Phase | 3.7 |  |  | SUITABLE FOR -3.73 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
13 | PASSAGE+DOUBLE HEIGHT -3 | ROOF TOP UNIT | 5886 | 16.55 | 3.7 | 1 | Three Phase | 3.7 |  |  | SUITABLE FOR -3.73 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 76 HP VRV OUTDOOR | TOP DISCHARGE |  | 26 HP | 19.9 | 2 | Three Phase | 39.8 |  | 63X2 |  | 4C X ( 16 Sqmm Cu).x 2 No with Neutral +Earth.- 2 No
|  |  |  | 24 HP | 17.3 | 1 | Three Phase | 17.3 |  | 63X1 |  | 4C X ( 16 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| IDU / ODU K.W ( CKT -5) | [6 empty] | 68.2
FIRST FLOOR
CKT - 6
14 | MASTER BEDROOM 1 | ROOF TOP UNIT | 2490 | 6.75 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
15 | MASTER BEDROOM 2 | ROOF TOP UNIT | 2576 | 7 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
14 | MASTER BATH +DRESS+WALK -1 | ROOF TOP UNIT | 2217 | 5.99 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
15 | MASTER BATH +DRESS+WALK -2 | ROOF TOP UNIT | 1894 | 4.98 | 1.5 | 1 | Three Phase | 1.5 |  |  | SUITABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 40 HP VRV OUTDOOR | TOP DISCHARGE |  | 20 HP | 17.9 | 2 | Three Phase | 35.8 |  | 63X2 |  | 4C X ( 16 Sqmm Cu).x 2 No with Neutral +Earth.- 2 No
| IDU / ODU K.W ( CKT -6) | [6 empty] | 43.9
CKT - 7
16 | FAMILY LOUNGE | ROOF TOP UNIT | 3092 | 8.57 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
17 | GLAM ROOM & DRESS-1 | ROOF TOP UNIT | 3000 | 8.57 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
GLAM BATH+TOILET -1
| BAR AREA LOBBY+ POWDER TOILET | ROOF TOP UNIT | 3613 | 10.06 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
18 | GUEST ROOM - 2 | ROOF TOP UNIT | 2500 | 6.23 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
GUEST TOILET & DRESS -2
| 52 HP VRV OUTDOOR | TOP DISCHARGE |  | 26 HP | 19.9 | 2 | Three Phase | 39.8 |  | 63X2 |  | 4C X ( 16 Sqmm Cu).x 2 No with Neutral +Earth.- 2 No
| IDU / ODU K.W ( CKT -7) | [6 empty] | 48.6
CKT - 8
19 | KIDS BEDROOM-1 | ROOF TOP UNIT | 1657 | 4.31 | 1.1 | 1 | Three Phase | 1.1 |  |  | SUITABLE FOR -1.12 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
20 | KIDS TOI & DRESS , WIW -1 | ROOF TOP UNIT | 1573 | 4.11 | 1.1 | 1 | Three Phase | 1.1 |  |  | SUITABLE FOR -1.12 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| KIDS BEDROOM-2+LOBBY | ROOF TOP UNIT | 1949 | 5.11 | 1.5 | 1 | Three Phase | 1.5 |  |  | SUITABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| KIDS TOI BATH+DRESS/ WIW -2 | ROOF TOP UNIT | 1464 | 3.79 | 1.1 | 1 | Three Phase | 1.1 |  |  | SUITABLE FOR -1.12 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 34 HP VRV OUTDOOR | TOP DISCHARGE |  | 20 HP | 17.9 | 1 | Three Phase | 17.9 |  | 63X1 |  | 4C X ( 16 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
|  |  |  | 14 HP | 10.6 | 1 | Three Phase | 10.6 |  | 32X1 |  | 4C X ( 16 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| IDU / ODU K.W ( CKT -8) | [6 empty] | 33.3
CKT - 9
21 | KIDS BEDROOM-3 | ROOF TOP UNIT | 1919 | 5.06 | 1.5 | 1 | Three Phase | 1.5 |  |  | SUITABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
22 | KIDS BEDROOM-4 | ROOF TOP UNIT | 2058 | 5.42 | 1.5 | 1 | Three Phase | 1.5 |  |  | SUITABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| KIDS TOILET & DRESS LOUNGE -3 |  | 1346 | 3.44 | 1.1 | 1 | Three Phase | 1.1 |  |  | SUITABLE FOR -1.12 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
23 | KIDS TOI+DRESS LOUNGE -4 | ROOF TOP UNIT | 1135 | 2.91 | 1.1 | 1 | Three Phase | 1.1 |  |  | SUITABLE FOR -1.12 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 32 HP VRV OUTDOOR | TOP DISCHARGE |  | 16 HP | 13.1 | 2 | Three Phase | 26.2 |  | 40X2 |  | 4C X ( 16 Sqmm Cu).x 2 No with Neutral +Earth.- 2 No
| IDU / ODU K.W ( CKT -9) | [6 empty] | 31.4
CKT - 10
24 | COMMON LOBBY+STAIRCASE -1 | ROOF TOP UNIT | 3533 | 9.83 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
25 | COMMON LOBBY+STAIRCASE -2 | ROOF TOP UNIT | 3533 | 9.83 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
26 | COMMON LOBBY+STAIRCASE -3 | ROOF TOP UNIT | 3533 | 9.83 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
26 | COMMON LOBBY+STAIRCASE -4 | ROOF TOP UNIT | 3533 | 9.83 | 2.2 | 1 | Three Phase | 2.2 |  |  | SUITABLE FOR -2.24 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 52 HP VRV OUTDOOR | TOP DISCHARGE |  | 26 HP | 19.9 | 2 | Three Phase | 39.8 |  | 63X2 |  | 4C X ( 16 Sqmm Cu).x 2 No with Neutral +Earth.- 2 No
| IDU / ODU K.W ( CKT -10) | [6 empty] | 48.6
| CKT - 11 | [9 empty] | -
27 | TFA FOR KITCHEN | ROOF TOP UNIT | 1900 | 12.2 | 1.49 | 1 | Three Phase | 1.5 |  |  | SUITABLE FOR -1.49 KW MOTOR | 4CX ( 6 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| 16 HP VRV OUTDOOR | TOP DISCHARGE |  | 16 HP | 13.1 | 1 | Three Phase | 13.1 |  | 40X1 |  | 4C X ( 10 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| IDU / ODU K.W ( CKT -11) | [6 empty] | 14.6
CKT - 12
29 | ELECTRICAL ROOM | HI-WALL | FXAQ50 | 1.65 | 0.4 | 1 | Single phase | 0.4 | 6 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
30 | STAFF LOUNGE | HI-WALL | FXAQ50 | 1.65 | 0.4 | 2 | Single phase | 0.7 | 6 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
29 | AV ROOM | HI-WALL | FXAQ25 | 0.83 | 0.4 | 1 | Single phase | 0.4 | 6 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
30 | SHOE ROOM | HI-WALL | FXAQ50 | 1.65 | 0.4 | 1 | Single phase | 0.4 | 6 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
29 | ELECTRICAL ROOM | HI-WALL | FXAQ63 | 2.08 | 0.4 | 1 | Single phase | 0.4 | 6 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
30 | MAIDROOM-1&2 | HI-WALL | FXAQ50 | 1.65 | 0.4 | 2 | Single phase | 0.7 | 6 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
29 | AV ROOM | HI-WALL | FXAQ63 | 2.08 | 0.4 | 2 | Single phase | 0.7 | 6 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
| 18 HP VRV OUTDOOR | TOP DISCHARGE |  | 18 HP | 15.5 | 1 | Three Phase | 15.5 |  | 40X1 |  | 4CX ( 16 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| IDU / ODU K.W ( CKT -12) | [6 empty] | 19.2
| TOTAL | VRV OUTDDOOR + AHU UNITS K.W | [5 empty] | 486.21
NON VRV
| ELECTRICAL ROOM (GF) | SPLIT AC |  | 1.5 | 1.8 | 1 | Single phase | 1.8 | 32 |  |  | 4CX ( 2.5 Sqmm Cu).x 4 No with Neutral +Earth.- 1 No
| ELECTRICAL ROOM (FF) | SPLIT AC |  | 2 | 2 | 1 | Single phase | 2 | 32 |  |  | 4CX ( 2.5 Sqmm Cu).x 1 No with Neutral +Earth.- 1 No
| KITCHEN(GF) | CASSATTE AC |  | 2 | 2 | 2 | Single phase | 4 | 32 |  |  | 4CX ( 2.5 Sqmm Cu).x 1 No with Neutral +Earth.- 2 No
| TOTAL | NON VRV | [5 empty] | 7.8
EXHUAST / FRASH AIR INLINE FAN
CFM
|  | CABINET TYPE | 100-200 |  | 0.3 | 14 | Single phase | 4.2 | 32 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
|  | CABINET TYPE | 200-500 |  | 0.5 | 13 | Single phase | 6.5 | 32 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
|  | CABINET TYPE | 500-1000 |  | 1 | 1 | Single phase | 1 | 32 |  |  | 3 Core x 2.5 Sqmm Cu. With gang box + earthing
| TOTAL | VENTILATION FAN | [5 empty] | 11.7
| GRAND TOTAL | [6 empty] | 505.71 | KW
NOTE-
REQUIRED INDOOR SEFTY DEVICE(SCANNER) AND ODU SCANNER WITH HI-LOW CUTOFF AND PHASE SEQUENCE.
* ODU's IKW at 100% Diversity at 43'C DB and Inside conditions at 240 CDB, 17'CWB.
* ELCB Rating (A) 300mA, 4 Pole.
* In place of PVC cable if XLPE cable will consider then pls have one size less.
*1 Rated capacity MCB should be provided
*2 Rated capacity MCCB should be provided
*3 Nominal size of Cu conductor, 4core XLPE insulated armoured cables 50 Hz. With Earthing,

## Plumbing
Rough power consumption list
SR | LOCATION | ITEM DESCRIPTION | UNIT | QTY | LOAD | REMARKS
1 | PUMP ROOM | Required for : RO water treatment (feed pump) | NO | 1 | 0.9
2 | TERRACE | RO SYSTEM PUMP |  | 1 | 2
3 | PUMP ROOM | UV-SYSTEM: Flow 1.5 M3/Hr with Run Hour Meter, MOC: Chamber-SS 304, Quartz Tube, Disinfection Efficiency-99.9%,UV Lamp Intensity-30, 000 Microwattsec/cm2, UV Lamp Life -7,500 Burning Hours, Accessories: UV intesity Monitor /Hr Meter | NO | 1 | 1
4 | TERRACE | Hydropneumatic system as follows: | NO | 1 | 2.2
5 | TERRACE | HEAT PUMP | NO | 2 | 30
6 | TERRACE | Hot water Return pump | NO | 1 | 0.75
7 | PUMP ROOM | Required for : Raw water treatment (feed pump) | NO | 1 | 0.75
8 | PUMP ROOM | Required for : Domestic water transfer | NO | 1 | 1.1
9 | PUMP ROOM | Purpose : Basement Storm water drainage | NO | 1 | 1.5
10 | PUMP ROOM | Required for : Rain water filter pump and transfer to Raw Water Tank | NO | 1 | 2.2
11
12
TOTAL KW |  |  |  |  | 42.4

## Water body & pool
Rough power consumption list
ELECTRICAL LOAD FOR WATER BODIES
S.No. | Discription | Qty | Voltage | Capacity (KW) | Working Load (KW) | Total Load (KW) | REMARKS
A | WATER BODY-1 (REAL SIDE) | ECP - 1 (INDOOR TYPE IN PLANT ROOM)
1 | Pump for Filtration (Cyclic Operation) | 2 No. (1W+1S) | 215-240V | 1.5 | 1.5 | 3
2 | Sump Pump for Plant Room | 1 No. | 215-240V | 1.1 | 1.1 | 1.1
3 | Doser (MCB Only) | 2 No. | 215-230V | 0.08 | 0.16 | 0.16
4 | Pump for Color Vision Bubbler Jets (Cyclic Operation) (For 37 No. Jets) | 3 No. (2W+1S) | 380-415V | 5.5 | 11 | 16.5
5 | U/W Led Color Vision Light | 37 No. | 12V | 0.015 | 0.56 | 0.56
6 | Pump for Color Vision Bubbler Jets (Cyclic Operation) (For 29 No. Jets) | 3 No. (2W+1S) | 380-415V | 5.5 | 16.5 | 16.5
7 | U/W Led Color Vision Light | 29 No. | 12V | 0.015 | 0.44 | 0.44
8 | Pump for Color Vision Bubbler Jets (Cyclic Operation) (For 37 No. Jets) | 3 No. (2W+1S) | 380-415V | 5.5 | 16.5 | 16.5
9 | U/W Led Color Vision Light | 37 No. | 12V | 0.015 | 0.56 | 0.56
11 | Spare Load |  |  |  | 7 | 7
| TOTAL LOAD |  |  |  | 55.32 | 62.32
B | WATER BODY-2 (KOI POND) | ECP - 2 (INDOOR TYPE IN PLANT ROOM)
1 | Pump for Filtration (Cyclic Operation) | 2 No. (1W+1S) | 380-415V | 2.2 | 2.2 | 4.4
2 | Air Blower for 60 Air Nozzle (Pneumatic Operated) | 2 No. (1W+1S) | 380-440V | 2.2 | 2.2 | 4.4
3 | UV System | 1 No. | 215-240V | 0.13 | 0.13 | 0.13
4 | Online Heater for Winter Season (MCB Only TPN) | 2 No. | 380-415V | 18 | 36 | 36
5 | Pump for Water Bowl in Side Koi Pond (Cyclic Operation) | 2 No. (1W+1S) | 215-230V | 2.2 | 2.2 | 4.4
6 | U/W LED Light, 12W / 12V AC for Bowl | 8 No. | 12V / AC | 0.012 | 0.1 | 0.1
6 | U/W LED Light, 12W / 12V AC for Koi Pond | 8 No. | 12V / AC | 0.012 | 0.1 | 0.1
7 | Spare Load |  |  |  | 7 | 7
| TOTAL LOAD |  |  |  | 49.93 | 56.53
C | WATER BODY-3 (NEAR POOJA DECK AREA) | ECP - 3 (INDOOR TYPE IN PLANT ROOM)
1 | Pump for Filtration (Cyclic Operation) | 2 No. (1W+1S) | 215-240V | 0.75 | 0.75 | 1.5
2 | Doser (MCB Only) | 2 No. | 215-230V | 0.08 | 0.16 | 0.16
3 | Pump for Diamond Cut Nozzles (Cyclic Operation) (For 13 No. Jets) | 2 No. (1W+1S) | 380-415V | 5.5 | 5.5 | 11
4 | Light for Diamond Cut Nozzles | 12 No. | 12V/24V | 0.012 | 0.14 | 0.14
5 | U/W LED Light, 14W / 12V AC For Water Body | 4 No. | 12V / AC | 0.012 | 0.05 | 0.05
6 | Spare Load |  |  |  | 2 | 2
| TOTAL LOAD |  |  |  | 8.6 | 14.85
D | WATER BODY-4 (NEAR POOJA DECK AREA) | ECP - 4 (INDOOR TYPE IN PLANT ROOM)
1 | Pump for Filtration (Cyclic Operation) | 2 No. (1W+1S) | 215-240V | 0.75 | 0.75 | 1.5
2 | Doser (MCB Only) | 2 No. | 215-230V | 0.08 | 0.16 | 0.16
3 | Pump for River Flow Effect Nozzle (Cyclic Operation) | 2 No. (1W+1S) | 380-415V | 3.75 | 3.75 | 7.5
4 | U/W LED Light, 12W / 12V AC | 10 No. | 12V / AC | 0.012 | 0.12 | 0.12
5 | Spare Load |  |  |  | 2 | 2
| TOTAL LOAD |  |  |  | 6.78 | 11.28
E | WATER BODY-5 (NEAR DROP OFF) | ECP - 5 (INDOOR TYPE IN PLANT ROOM)
1 | Pump for Filtration (Cyclic Operation) | 2 No. (1W+1S) | 215-240V | 0.75 | 0.75 | 1.5
2 | Doser (MCB Only) | 2 No. | 215-230V | 0.08 | 0.16 | 0.16
3 | Pump for Rain Effects Water Cascade (Cyclic Operation) | 2 No. (1W+1S) | 380-415V | 3.75 | 3.75 | 7.5
4 | U/W LED Light, 12W / 12V AC | 10 No. | 12V / AC | 0.014 | 0.14 | 0.14
5 | Spare Load |  |  |  | 2 | 2
| TOTAL LOAD |  |  |  | 6.8 | 11.3
F | WATER BODY-6 (BREAKFAST WOODEN DECK) | ECP - 6 (INDOOR TYPE IN PLANT ROOM)
1 | Pump for Filtration (Cyclic Operation) | 2 No. (1W+1S) | 215-240V | 0.75 | 0.75 | 1.5
2 | Doser (MCB Only) | 2 No. | 215-230V | 0.08 | 0.16 | 0.16
3 | Pump for Feature Wall (Cyclic Operation) | 2 No. (1W+1S) | 380-415V | 3.75 | 3.75 | 7.5
4 | U/W LED Stand Light, 12W / 12V AC | 5 No. | 12V / AC | 0.012 | 0.06 | 0.06
5 | Spare Load |  |  |  | 2 | 2
| TOTAL LOAD |  |  |  | 6.72 | 11.22
G | SWIMMING POOL | ECP - 7 (INDOOR TYPE IN PLANT ROOM)
1 | Pump for Filtration (Cyclic Operation) | 2 No. (1W+1S) | 215-240V | 3.75 | 3.75 | 7.5
2 | Pump for Sliding (Cyclic Operation) | 2 No. (1W+1S) | 215-240V | 2.2 | 2.2 | 4.4
3 | UV System (MCB Only) | 2 No. | 215-230V | 0.075 | 0.15 | 0.15
4 | Ozone Generator (MCB Only) | 2 No. | 215-230V | 0.5 | 1 | 1
5 | U/W LED Light, for Pool | 20 No. |  | 0.012 | 0.24 | 0.24 | Appx Load (Not in BOQ)
6 | Spare Load |  |  |  | 3 | 3
| TOTAL LOAD |  |  |  | 10.34 | 16.29
| GRAND TOTAL |  |  |  | 144.49 | 183.79
| SAY |  |  |  | 145 | 184

## GF & FF load
Rough power consumption list
SR NO. | AREA | LOCATION | UNIT | MODEL NO | Ceiling Light | 6A AUTOMATION SOCKET | 06/13A SOCKET | FAN REGULATOR | FOOT LIGHT | 6A SOCKET Automation | 06/13A SOCKET | 16A SOCKET | REMARKS
1 | GF | Living Room & Bar | No. |  |  | 1 | 1 |  |  |  |  | 1
|  |  | No. |  |  | 2 | 2 |  |  |  |  | 2
|  |  | No. |  |  | 1
|  |  | No. |  |  |  | 1 |  |  |  | 0 | 0
|  |  | No. |  |  | 1 | 2
2 | GF | Guruji Bedroom | No. |  |  | 1 | 1 |  |  |  | 0 | 0
|  |  | No. |  |  | 1
|  |  | No. |  |  | 4 | 1 | 1 |  | 2 | 2 | 0
3 | GF | Guruji Bedroom Toilet | No. |  |  | 2 |  |  | 1
No.
4 | GF | Guest Bedroom | No. |  |  | 1 | 2 |  |  |  | 0 | 0
|  |  | No. |  |  | 1
|  |  | No. |  |  | 4 |  | 1 |  | 2 | 2 | 0
No.
5 | GF | Guest Bedroom Toilet | No. |  |  | 2 | 0 | 0
|  |  | No. |  |  |  | 1
1
|  |  | No. |  |  | 3 |  |  | 1
[6 empty] | 2 | 1
6 | GF | Master Bedroom-2 | No. |  |  |  | 2 |  |  |  | 0 | 0
|  |  | No. |  |  |  | 1
|  |  | No. |  |  | 6 |  | 1 |  | 2 | 2 | 0
7 | GF | Master Bedroom-2 Dresser | No. |  |  | 1 | 1
|  |  | No. |  |  | 2
|  |  | No. |  |  | 1
|  |  | No. |  |  | 1
8 | GF | Master Bedroom-2 Toilet | No. |  |  | 1 |  |  |  |  | 1
|  |  | No. |  |  | 1 | 2
|  |  | No. |  |  | 4 | 2
|  |  | No. | [5 empty] | 1
|  |  | No. |  |  | 2
9 | GF | Master Bedroom-1 | No. |  |  |  | 3 |  |  |  | 0 | 0
No.
|  |  | No. |  |  | 1 |  | 1 |  | 2 | 2 | 0
|  |  | No. |  |  | 1
|  |  | No. |  |  | 1
10 | GF | Master Bedroom-1 toilet | No. |  |  | 4 | 1
No.
|  |  | No. |  |  | 2 | 2
|  |  | No. | [5 empty] | 1
|  |  | No. |  |  |  | 2
|  |  | No. |  |  | 3 | 2
11 | GF | Family Lounge | No. |  |  | 2
|  |  | No. |  |  | 6 | 3 |  |  |  | 0 | 0
12 | GF | Study Room | No. | [6 empty] | 1 | 0 | 1
|  |  | No. |  |  | 1
|  |  | No. |  |  |  | 1
13 | GF | Kitchen | No. |  |  | 1
14 | GF | Powder Toilet 3 | No. |  |  | 2 | 1
15 | GF | Staff area | No. |  |  | 1 | 7 |  |  |  |  | 2
16 | GF | Dinning Room | No. |  |  |  | 4 |  |  |  |  | 2
17 | GF | Dinning room powder toilet | No. |  |  | 1 | 2 |  |  |  |  | 1
18 | GF | Master Dresser-1 | No. |  |  | 1 | 1
19 | GF | Entrance Loby | No. |  |  | 1 | [5 empty] | 1
20 |  | GF Passage |  |  |  | 4 | 10 |  |  |  |  | 2
21 | GF | Bar Room Powder Toilet | No. |  |  |  | 1 |  |  |  |  | 1
| GF | Pooja Room | No. |  |  | 2 | 8 |  |  |  |  | 1
22 | FF | Passage |  |  |  |  | 10 |  |  |  |  | 2 | Dwg are pending for switch socket qty. I taked as per GF Dwg
23 | FF | Bar Area-1 | No. |  |  |  | 5 |  |  |  |  | 2
24 | FF | Powder Room near Bar | No. |  |  | 1 | 1 |  |  |  |  | 1
25 | FF | Formal Living room | No. |  |  | 1 | 8 |  |  |  |  | 2
26 | FF | Pantry Near Bar | No. |  |  | 1
27 | FF | Kids Bedroom-4 | No. |  |  | 4 | 6 |  |  |  |  | 2
28 | FF | Kids Toilet-4 & Dresser | No. |  |  |  | 4 |  |  |  |  | 1
29 | FF | Loby Near Kids Bedroom-4 | No. |  |  | 2 | 2 |  |  | 0 |  | 1
30 | FF | Kids Bedroom3- | No. |  |  |  | 6 |  |  |  |  | 2
31 | FF | Kids Toilet-3 Dresser | No. |  |  |  | 4 |  |  |  |  | 1
32 | FF | Main Lift Loby Gf & FF | No. |  |  | 3 | 1 |  |  |  |  | 1
33 | FF | Master Bedroom-2 | No. |  |  | 2 | 5 |  |  |  |  | 1
34 | FF | Master Bedroom Toilet-2 Wiw | No. |  |  |  | 7 |  |  |  |  | 1
35 | FF | Master Bedroom-1 |  |  |  |  | 5 |  |  |  |  | 1
36 | FF | Master Bedroom Toilet-1 Wiw |  |  |  | 6 | 7 |  |  |  |  | 1
37 | FF | Kids bedroom-2 loby area | No. |  |  | 1 | 1 |  |  |  |  | 1
38 | FF | Kids bedroom-2 | No. |  |  | 1 | 6 |  |  |  |  | 2
39 | FF | Kids Toilet-2 | No. |  |  | 1 | 4 |  |  |  |  | 1
40 | FF | Kids Bedroom-1 | No. |  |  | 4 | 6 |  |  |  |  | 2
41 | FF | Kids Bedroom-1 Toilet & dreeser | No. |  |  |  | 4 |  |  |  |  | 1
42 | FF | Pantry | No. |  |  | 2
43 | FF | Glam Room | No. |  |  |  | 4 |  |  |  |  | 2
44 | FF | Glam Room Toilet & dresser |  |  |  |  | 2 |  |  |  |  | 1
45 | FF | Guest Bedroom | No. |  |  | 3 | 6 |  |  |  |  | 2
46 | FF | Guest Bathroom | No. |  |  | 2 | 4 |  |  |  |  | 1
TOTAL QTY | [5 empty] | 113 | 177 | 4 | 4 | 9 | 9 | 46
TOTAL QTY | [5 empty] | 6.78 |  |  |  |  | 186 | 46
|  | Load KW | [8 empty] | 18.6 | 23
Total Load KW | [11 empty] | 41.6

## Kitchen Pantry
Rough power consumption list
PROPOSED APPLIANCES | SUPPLIER | CODE | QTY. | Load KW | TOTAL KW | Remarks
BUILT-IN HOB 90CM | GAGGENAU | VG 491 111IN | 1 | 0.1 | 0.1
BUILT-IN HOB 38CM | GAGGENAU | VG 425 111IN | 1 | 0.1 | 0.1
BUILT-IN HOB 38CM | GAGGENAU | VG 415 111IN | 1 | 0.1 | 0.1
BUILT-IN GRILL 38CM | GAGGENAU | VR 414 115 | 1 | 0.1 | 0.1
ISLAND CHIMNEY 120CM | GAGGENAU | AC 250 121 | 1 | 0.3 | 0.3
FOR CHIMNEY | GAGGENAU | AR 401 142 | 3 | 1 | 3
VARIO DOWN DRAFT VENTILATION | GAGGENAU | VL 414 115 | 2 | 0.3 | 0.6
BUILT-IN MICROWAVE 60CM | GAGGENAU | BMP 224 100 | 2 | 2 | 4
BUILT-IN OVEN 60CM | GAGGENAU | BOP 250 102 | 1 | 4 | 4
BUILT-IN WARMER DRAWER 14CM | GAGGENAU | WSP 221 102 | 3 | 1 | 3
BUILT-IN COFFEE MAKER 60CM | GAGGENAU | CMP 250 102 | 1 | 1.6 | 1.6
BUILT-IN FRIDGE 75.6CM | GAGGENAU | RC 472 304 | 1 | 0.5 | 0.5
BUILT-IN FRIDGE 75.6CM | GAGGENAU | RB 472 305 | 1 | 0.5 | 0.5
BUILT-IN DISHWASHER 60CM | GAGGENAU | DF 270 101F | 1 | 2.2 | 2.2
DISHWASHING ACC. | GAGGENAU | DA 041 160 | 1 |  | 0
COMMERCIAL DISHWASHER IN WASH AREA |  |  | 1 | 3.5 | 3.5
ICE MAKER MACHINE IN WASH AREA |  |  | 1 | 1 | 1
FREE STANDING FRIDGE IN STORE |  |  | 2 | 1 | 2
DEEP FREEZER IN CROCKERY ROOM |  |  | 1 | 1.5 | 1.5
General Purpose use switch socket 16A |  |  | 20 | 0.5 | 10
FF PANTRY-1 & 2
Microwave 60cm |  |  | 2 | 2 | 4
Oven 60cm |  |  | 2 | 4 | 8
Built-in chimney 90cm |  |  | 1 | 0.3 | 0.3
Wall chimney 90cm |  |  | 1 | 0.3 | 0.3
Induction 60cm |  |  | 2 | 7 | 14
Built-in fridge 60cm |  |  | 2 | 0.5 | 1
General Purpose use switch socket 16A |  |  | 10 | 0.5 | 5
SUB TOTAL KW |  |  |  |  | 70.7

## LIFT
Rough power consumption list
SR | LOCATION | TYPE | KW | REMARKS
1 | MAIN BUILDING | PASSENGER LIFT | 3.7
2 | MAIN BUILDING | SERVICE LIFT | 3.7
|  | TOTAL | 7.4
8

## Landscape Lighting
Rough power consumption list
Sr no. | Area | Light Module | Light Type | UNIT | QTY AS PER DWG:08/01/2026 | LIGHT WATT | Total KW | POWER WATT | Total KW | REMARKS
1 | Landscape | XL-01 | Wall lights - Ceiling - surface mount type light | No. | 4 | 11.2 | 0.0448
2 | Landscape | XL-02 | SURFACE MOUNTING TYPE LIGHT | No. | 143 | 8 | 1.144
3 | Landscape | XL-02-2 | SURFACE MOUNTING TYPE LIGHT | No. | 40 | 3 | 0.12
4 |  | XL-02-3 | SURFACE MOUNTING TYPE LIGHT | No. | 6 | 3 | 0.018
|  | XL-02-4 |  | No. | 14 | 13 | 0.182
5 | Landscape | XL-03 | LIGHT CANCELLED | No. | 0 | 12 | 0
6 | Landscape | XL-04 | BOLLARD & POLE | No. | 13 |  | 0
7 | Landscape | XL-04A | FLOOR LAMP BOLLARD | No. | 7 | 10 | 0.07
8 | Landscape | XL-04B | FLOOR LAMP BOLLARD | No. | 6 | 22 | 0.132
9 | Landscape | XL04C |  | No. | 0 |  | 0
10 | Landscape | XL-05 | Drive Over | No. | 11 | 8 | 0.088
11 | Landscape | XL-06 | FRAME | No. | 20 | 1.7 | 0.034
12 | Landscape | XL-07B | Frameless | No. | 2 | 19.5 | 0.039
13 | Landscape | XL07A/XL-1A | Frameless | No. | 36 | 26 | 0.936
14 | Landscape | XL-08 | Semi-recessed - Step | No. | 23 | 8.2 | 0.1886
15 | Landscape | XL-09 | Bollard & Pole | No. | 17 | 12 | 0.204
16 | Landscape | XL-10 | Encasement with flange | No. | 4 | 8 | 0.032
17 | Landscape | XL-11 | Surface Wall lights - Ceiling | No. | 13 | 3 | 0.039
18 | Landscape | XL-12 | Downlights-Encasement without flange-Walk Over - Lines - Surface | No. | 21 | 6.7 | 0.1407
19 | Landscape | XL-13 | LED Strip cove light | Mtr | 112 | 3.2 | 0.3584
20 | Landscape | XL-14 | Frameless | No. | 80 | 26 | 2.08
21 | Landscape | XL-15-1 | Bollard | No. | 7 | 1.5 | 0.0105
22 | Landscape | XL-15-2 | Bollard | No. | 5 | 1.5 | 0.0075
23 | Landscape | XL-16 | Bollard | No. | 4 | 4 | 0.016
24 | Landscape | XL-16A | Bollard | No. | 6 | 4 | 0.024
25 | Landscape | XL-16B | Bollard | No. | 5 | 4 | 0.02
26 | Landscape | XL-17 | CANCELLED | No. |  | 26.5 | 0
27 | Landscape | XL-18 | Encasement with flange - Step Light | No. | 6 | 2 | 0.012
28 | Landscape | GR-X01 | Walk Over concealed light | No. | 6 | 4 | 0.024
29 | Landscape | CR-01 | Encasement with flange, Ceiling Light | No. | 8 | 9 | 0.072
30 | Landscape | XL-14 |  | No. | 8 |  | 0
31 | Landscape | GR-X09 | Frameless concealed light | No. | 2 | 14 | 0.028
32 | Pole Light | Pole Light |  | No. | 12 | 36 | 0.432
TOTAL
Power Switch for Landscape
1 | West side Boundry | 16A | Switch socket | No. | 10 |  |  | 500 | 5
| North side Boundry | 16A | Switch socket | No. | 5 |  |  | 500 | 2.5
| East side | 16A | Switch socket | No. | 10 |  |  | 500 | 5
| South Side | 16A | Switch socket | No. | 5 |  |  | 500 | 2.5
Glass House
1 | 6A Switch socket | 6A | Switch socket | No. | 4 | 200 | 0.8
2 | Casate Ac unit | 1.5 Ton Ac | NON VRV DUCTABLE 1.5TR | No. | 4 |  |  | 1500 | 6
3 | Ceiling Light | [5 empty] | 0
| 16A socket | 16A | Switch socket | No. | 1 |  |  | 500 | 0.5
His & Her Toilet
1 | Ac indoor Ductable unit | AC | 0.38 ton AC | Nos | 2 |  |  | 380 | 0.76
| Outdoor | AC | 3 phase | Nos | 1 |  |  | 5300 | 5.3
| Socket 16A | 16A | Switch Socket | Nos | 8 |  |  | 500 | 4
| Socket 6A | 6A | Switch Socket | Nos | 8 | 200 | 1.6
| Ceiling Light | Ceiling Light | Ceiling Light | Nos | 28 | 10 | 0.28
Bar Room
| 6A Switch socket | 6A | Switch socket | Nos | 6 | 200 | 1.2
| 16 A Switch socket | 16A | Switch socket | Nos | 10 |  |  | 500 | 5
| Light Point | Light points | Floor Light | Nos | 13 | 7 | 0.091
| Ceiling Light | Ceiling Light | Ceiling Light | Nos | 10 | 7 | 0.07
Catring zone
1 | Split Ac Load | 1.5 Ton ac | AC | Nos | 2 |  |  | 2000 | 4
2 | 16 A Switch socket |  |  |  | 3 |  |  | 1000 | 3
3 | 6 A Switch socket |  |  |  | 3 | 200 | 0.6
4 | 16 amp socket for Hood in ceiling |  |  | Nos | 2 | 200 | 0.4
5 | 16 amp socket for HOB at floor |  |  | Nos | 2 | 100 | 0.2
6 | 16A switch socket | 16A | Refrigerator | Nos | 5 |  |  | 800 | 4
7 | 16 amp. socket for steam oven and warming drawer-2No. | 16A |  | Nos | 2 |  |  | 1200 | 2.4
8 | Ceiling Light | Light points | Wall Lights | Nos | 10 | 100 | 1
Gard Room
1 | 16A Switch socket | 16A | 16A switch socket | Nos | 3 |  |  | 1000 | 3
2 | 6A Switch socket | 6A | 6A switch socket | Nos | 5 | 200 | 1
3 | Ceiling Light | ceiling Light | Ceiling Light | Nos | 4 | 10 | 0.04
4 | Split Ac | 1.5 TR | AC | Nos | 1 |  |  | 2000 | 2
| Driver Lounge | [5 empty] | 0
1 | 16A Switch socket | 16A Switch socket | 16A switch socket | Nos | 2 |  |  | 1000 | 2
2 | 6A Switch socket | 6A | 6A switch socket | Nos | 4 | 200 | 0.8
3 | Ceiling Light | ceiling Light | Light | Nos | 4 | 10 | 0.04
Car Parking
1 | EV Car charging |  |  | Nos | 2 |  |  | 3300 | 6.6
LT Room
1 | Split Ac | 1.5 TR ac | Ac | Nos | 2 |  |  | 2000 | 4
2 | 16A Switch socket | 16A | Switch socket | Nos | 4 |  |  | 1000 | 4
3 | 6A Switch socket | 6A | Switch socket | Nos | 2 | 200 | 0.4
4 | Light |  |  | Nos | 4 | 10 | 0.04
TOTAL LOAD | [6 empty] | 15.0575 |  | 71.56

## Internal Light
Rough power consumption list
SR NO. | AREA | LOCATION | UNIT | GR-X01 | GR-X02 | GR-X03 | GR-X04 | GR-X05 | GR-X06 | GR-X07 | GR-X08 | GR-X09 | SM-X01 | REMARKS
1 | GF | Master toilet-1 Green area | No. | 8
2 | GF | Family Lounge & study area | No. |  | 1 | 1 | 0 |  | 3 |  | 0 |  | 21
3 | GF | Staff Lounge & Kitchen | No. |  | 3 |  |  | 2 | 1 |  |  |  | 29.9
4 | GF | Dinning Area | No. | [6 empty] | 1 |  | 2
5 | GF | Shoe cabinet loby | No. |  |  |  |  | 3 |  | 1
6 | GF | Entrance & Pooja Room | No. | 5 | [7 empty] | 2
7 | GF | Formal living & bar room | No. |  | 3 | 2 |  |  | 1 |  |  |  | 34.3
8 | GF | Loby | No. |  |  |  |  | 2
9 | GF | Guruji bedroom | No. |  | 1 | 2 | [6 empty] | 9.4
10 | GF | Loby | No. |  |  |  |  | 2
11 | GF | Guest Bedroom | No. |  | 1 | 2 | [6 empty] | 9.4
12 | GF | Master Bedroom -1 & 2 | No. |  | 3 |  |  |  | 1 |  |  | 4
13 | FF | Kids bedroom -1 &2 balcony | No. | 0 | 3 | 0 | 7 |  | 10
14 | FF | Servant room & glam room balcony | No. | 0 | 2 | 1 | 7 |  | 1
15 | FF | Cut out below | No. | 0 | 0 | 0 | 0 |  | 0 |  | 2
16 | FF | Family Lounge & Bar Room Balcony | No. | 0 | 4 | 2 | 5 |  | 2 |  | 0
17 | FF | Kids Bedroom-4 & 3 | No. | 0 | 2 | 2 | 0 |  | 0 |  | 0 |  |  |  | 220
18 | FF | Master Bedroom 2 | No. | 0 | 2 | 0 | 0 |  | 0 |  | 0
19 | FF | Master Bedroom 1 | No. | 0 | 2 | 0 | 0 |  | 0 |  | 0 |  |  |  | 70
TOTAL |  |  |  | 13 | 27 | 12 | 19 | 9 | 19 | 2 | 2 | 8 | 104
|  | WATTAGE AS PER FIXTURE |  | 41 | 16.5 | 8.3 | 3 | 41 | 33.2 | 41 | 9 | 14 | 9.6
|  | KW AS PER FIXTURE |  | 0.533 | 0.4455 | 0.0996 | 0.057 | 0.369 | 0.6308 | 0.082 | 0.018 | 0.112 | 0.9984
|  | LIGHT QTY |  | 6
|  | CHANDELLER |  | 9
TOTAL KW |  |  |  | 18.3453

## AUDIO VIDEO
Rough power consumption list
Particulars | Total Power (Watts) | Total Power (KW)
GROUND FLOOR
General zone (AV Rack) | 8 KV (approx) | 8
Puja area (on wall speakers - to be decided) | 2 KV (approx) | 2
Guruji's bedroom (75" TV with soundbar and subwoofer) | 1 KV | 1
Guest bedroom 1 (75" TV with soundbar and subwoofer) | 1 KV | 1
Master Bedroom 1 (97" TV with soundbar and subwoofer) | 1.5 KV | 1.5
Master Lounge 1 (97" TV with soundbar and subwoofer) 1 sonos amp taken for four in-ceiling speakers | 2 KV | 2
Master Bedroom 2 (97" TV with soundbar and subwoofer) | 1.5 KV | 1.5
Master Lounge 2 (97" TV with soundbar and subwoofer) 1 sonos amp taken for four in-ceiling speakers | 2 KV | 2
Bar area (97" TV with four in-ceiling speakers & 1 subwoofer) Formal living (six in-ceiling speakers & 2 subwoofer) | 5 KV (approx) | 5
Family Lounge (165" LED wall with speaker equipments) | 13.5 KV (approx) | 13.5
Play / Study area | 1 KV | 1
Double Height Courtyard (Pop up TV) | 2 KV (approx) | 2
FIRST FLOOR
Bar area (LED wall with speaker equipments) | 10 KV (approx) | 10
Formal Living (LED wall with speaker equipments) | 13.5 KV (approx) | 13.5
Guest bedroom (75" TV with soundbar and subwoofer) 1 sonos amp taken for two in-ceiling speakers | 1.5 KV | 1.5
Glam room | 1 KV | 1
Master Bedroom 1 (97" TV with soundbar and subwoofer) | 1.5 KV | 1.5
Master Lounge 1 (97" TV with soundbar and subwoofer) 1 sonos amp taken for two in-ceiling speakers | 2 KV | 0.2
Master Bedroom 2 (97" TV with soundbar and subwoofer) | 1.5 KV | 1.5
Master Lounge 2 (97" TV with soundbar and subwoofer) 1 sonos amp taken for two in-ceiling speakers | 2 KV | 0.2
Kids bedroom 1 (83" TV with soundbar and subwoofer) 1 sonos amp taken for two in-ceiling speakers | 1.5 KV | 1.5
Kids bedroom 2 (97" TV with soundbar and subwoofer) 1 sonos amp taken for two in-ceiling speakers | 1.5 KV | 1.5
Kids bedroom 3 (83" TV with soundbar and subwoofer) 1 sonos amp taken for two in-ceiling speakers | 1.5 KV | 1.5
Kids bedroom 4 (83" TV with soundbar and subwoofer) 1 sonos amp taken for two in-ceiling speakers | 1.5 KV | 1.5
ROUGH TOTAL POWER REQUIREMENT | 79.5 KV (approx)
LANDSCAPE AREA
Party area | 15 KV (approx) | 15
Koi pound
Glass House
Breakfast area
TOTAL IN KW LOAD |  | 90.9